## parameters
| version | converged | name | f_hz | sn_mva | OPF_converged
0 | 2.4.0 | TRUE |  | 50 | 1 | FALSE

## bus
| name | vn_kv | type | zone | in_service
0 | MA_1_L | 132 | b |  | TRUE
1 | MA_1_H | 220 | b |  | TRUE
2 | MA_2 | 220 | b |  | TRUE
3 | MA_3 | 220 | b |  | TRUE
4 | MA_4 | 220 | b |  | TRUE
5 | MA_5 | 220 | b |  | TRUE
6 | MA_6 | 220 | b |  | TRUE
7 | MA_7 | 220 | b |  | TRUE
8 | MA_8 | 220 | b |  | TRUE
9 | MA_9_L | 132 | b |  | TRUE
10 | MA_9_H | 220 | b |  | TRUE
11 | MA_10 | 132 | b |  | TRUE
12 | ME_1 | 132 | b |  | TRUE
13 | ME_2 | 132 | b |  | TRUE
14 | ME_3 | 132 | b |  | TRUE
15 | ME_4 | 132 | b |  | TRUE
16 | ME_5 | 132 | b |  | TRUE
17 | IB_1 | 132 | b |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | MA_1 Load | 0 | 34 | 16.4662 | 0 | 0 |  | 1 | TRUE | wye
1 | MA_1 Reactor | 0 | 0 | 200 | 0 | 0 |  | 1 | TRUE | wye
2 | MA_2 Load | 2 | 27 | 13.0761 | 0 | 0 |  | 1 | TRUE | wye
3 | MA_3 Load | 3 | 73.5 | 35.596 | 0 | 0 |  | 1 | TRUE | wye
4 | MA_4 Load | 4 | 91 | 44.0713 | 0 | 0 |  | 1 | TRUE | wye
5 | MA_5 Load | 5 | 56.5 | 27.363 | 0 | 0 |  | 1 | TRUE | wye
6 | MA_6 Load | 6 | 34 | 16.4662 | 0 | 0 |  | 1 | TRUE | wye
7 | MA_7 Load | 7 | 54 | 26.1522 | 0 | 0 |  | 1 | TRUE | wye
8 | MA_8 Load | 8 | 36 | 19.8563 | 0 | 0 |  | 1 | TRUE | wye
9 | MA_9 Load | 9 | 63 | 32.9324 | 0 | 0 |  | 1 | TRUE | wye
10 | MA_10 Load | 11 | 21 | 10.1703 | 0 | 0 |  | 1 | TRUE | wye
11 | ME_1 Load | 12 | 9 | 4.3587 | 0 | 0 |  | 1 | TRUE | wye
12 | ME_2 Load | 13 | 11 | 5.3273 | 0 | 0 |  | 1 | TRUE | wye
13 | ME_3 Load | 14 | 3 | 1.4529 | 0 | 0 |  | 1 | TRUE | wye
14 | ME_4 Load | 15 | 22 | 10.6546 | 0 | 0 |  | 1 | TRUE | wye
15 | ME_5 Load | 16 | 5 | 2.4215 | 0 | 0 |  | 1 | TRUE | wye
16 | IB_1 Load | 17 | 101 | 48.9143 | 0 | 0 |  | 1 | TRUE | wye

## sgen
| name | bus | p_mw | q_mvar | sn_mva | scaling | in_service | type | current_source
0 | MA_3 Generation | 3 | 97 | 46.9771 |  | 1 | TRUE | wye | TRUE
1 | MA_5 Generation | 5 | 61 | 29.5423 |  | 1 | TRUE | wye | TRUE
2 | MA_6 Generation | 6 | 16 | 7.7488 |  | 1 | TRUE | wye | TRUE
3 | MA_4 Generation | 4 | 13 | 6.2959 |  | 1 | TRUE | wye | TRUE
4 | MA_9 Generation | 9 | 104 | 50.3672 |  | 1 | TRUE | wye | TRUE
5 | MA_8 Generation | 8 | 96 | 46.4928 |  | 1 | TRUE | wye | TRUE
6 | MA_7 Generation | 7 | 39 | 18.8877 |  | 1 | TRUE | wye | TRUE
7 | ME_2 Generation | 13 | 92 | 44.5556 |  | 1 | TRUE | wye | TRUE
8 | IB_1 Generation | 17 | 45 | 21.7935 |  | 1 | TRUE | wye | TRUE

## ext_grid
| name | bus | vm_pu | va_degree | in_service
0 | Swing Bus 1 | 1 | 1 | 0 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | Line1_MA_1_IB_1 |  | 0 | 17 | 126 | 0.06 | 0.144 | 144 | 0 | 0.588 | 1 | 1 |  | TRUE
1 | Line2_MA_1_IB_1 |  | 0 | 17 | 126 | 0.06 | 0.144 | 144 | 0 | 0.588 | 1 | 1 |  | TRUE
2 | Line_MA_10_ME_1 |  | 11 | 12 | 41.8 | 0.06 | 0.144 | 144 | 0 | 0.588 | 1 | 1 |  | TRUE
3 | Line_ME_1_2 |  | 12 | 13 | 8.3 | 0.1188 | 0.39 | 9 | 0 | 0.645 | 1 | 1 |  | TRUE
4 | Line_ME_2_3 |  | 13 | 14 | 21.1 | 0.1188 | 0.39 | 9 | 0 | 0.645 | 1 | 1 |  | TRUE
5 | Line_ME_2_4 |  | 13 | 15 | 35.5 | 0.1188 | 0.39 | 9 | 0 | 0.645 | 1 | 1 |  | TRUE
6 | Line_ME_3_4 |  | 14 | 15 | 15.5 | 0.1188 | 0.39 | 9 | 0 | 0.645 | 1 | 1 |  | TRUE
7 | Line_ME_4_5_1 |  | 15 | 16 | 2.6 | 0.1188 | 0.39 | 9 | 0 | 0.645 | 1 | 1 |  | TRUE
8 | Line_ME_4_5_2 |  | 15 | 16 | 2 | 0.1188 | 0.39 | 9 | 0 | 0.645 | 1 | 1 |  | TRUE
9 | Line_MA_1_2 |  | 1 | 2 | 6.2 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
10 | Line_MA_2_3_1 |  | 2 | 3 | 15.4 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
11 | Line_MA_2_3_2 |  | 2 | 3 | 14.8 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
12 | Line_MA_3_4 |  | 3 | 4 | 9 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
13 | Line_MA_5_4 |  | 5 | 4 | 7.4 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
14 | Line_MA_6_4 |  | 6 | 4 | 4 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
15 | Line_MA_3_7 |  | 3 | 7 | 33.7 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
16 | Line_MA_4_7 |  | 4 | 7 | 28.8 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
17 | Line_MA_7_8_1 |  | 7 | 8 | 16.6 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
18 | Line_MA_7_8_2 |  | 7 | 8 | 16 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
19 | Line_MA_7_9_1 |  | 7 | 10 | 15 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
20 | Line_MA_7_9_2 |  | 7 | 10 | 15.4 | 0.059 | 0.285 | 10 | 0 | 0.96 | 1 | 1 |  | TRUE
21 | Line_MA_9_10 |  | 9 | 11 | 30.3 | 0.1188 | 0.39 | 9 | 0 | 0.645 | 1 | 1 |  | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 |  |  | 1 | 0 | 400 | 220 | 132 | 10 | 1 | 4 | 1 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE
1 |  |  | 10 | 9 | 400 | 220 | 132 | 10 | 1 | 4 | 1 | 0 | [7 empty] | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1
0 | 1.4312 | 38.9192 | 2.5089 | 39.5377
1 | 1.4312 | 38.9192 | 2.5089 | 39.5377
2 | 3.4273 | 39.7388 | 3.8338 | 39.932
3 | 3.8338 | 39.932 | 3.8555 | 40.0032
4 | 3.8555 | 40.0032 | 4.0958 | 39.9771
5 | 3.8555 | 40.0032 | 4.2371 | 39.891
6 | 4.0958 | 39.9771 | 4.2371 | 39.891
7 | 4.2371 | 39.891 | 4.2579 | 39.8972
8 | 4.2371 | 39.891 | 4.2579 | 39.8972
9 | 2.5089 | 39.5377 | 2.5494 | 39.5842
10 | 2.5494 | 39.5842 | 2.6788 | 39.651
11 | 2.5494 | 39.5842 | 2.6788 | 39.651
12 | 2.6788 | 39.651 | 2.7443 | 39.6
13 | 2.7024 | 39.5478 | 2.7443 | 39.6
14 | 2.7257 | 39.5683 | 2.7443 | 39.6
15 | 2.6788 | 39.651 | 3.0395 | 39.6736
16 | 2.7443 | 39.6 | 3.0395 | 39.6736
17 | 3.0395 | 39.6736 | 3.0925 | 39.8096
18 | 3.0395 | 39.6736 | 3.0925 | 39.8096
19 | 3.0395 | 39.6736 | 3.1586 | 39.5818
20 | 3.0395 | 39.6736 | 3.1586 | 39.5818
21 | 3.1586 | 39.5818 | 3.4273 | 39.7388

## bus_geodata
| x | y | coords
0 | 2.5089 | 39.5377
1 | 2.5089 | 39.5377
2 | 2.5494 | 39.5842
3 | 2.6788 | 39.651
4 | 2.7443 | 39.6
5 | 2.7024 | 39.5478
6 | 2.7257 | 39.5683
7 | 3.0395 | 39.6736
8 | 3.0925 | 39.8096
9 | 3.1586 | 39.5818
10 | 3.1586 | 39.5818
11 | 3.4273 | 39.7388
12 | 3.8338 | 39.932
13 | 3.8555 | 40.0032
14 | 4.0958 | 39.9771
15 | 4.2371 | 39.891
16 | 4.2579 | 39.8972
17 | 1.4312 | 38.9192

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98414 | -1.2539 | 34 | 216.4662
1 | 1 | 0 | -82.1952 | 4.5574
2 | 1.0023 | -0.0058512 | 27 | 13.0761
3 | 1.0059 | 0.049875 | -23.5 | -11.3811
4 | 1.006 | -0.047711 | 78 | 37.7754
5 | 1.0062 | -0.038016 | -4.5 | -2.1793
6 | 1.0058 | -0.069396 | 18 | 8.7174
7 | 1.0166 | 0.43464 | 15 | 7.2645
8 | 1.0186 | 0.57786 | -60 | -26.6365
9 | 1.0375 | 1.2778 | -41 | -17.4348
10 | 1.02 | 0.55073 | 0 | 0
11 | 1.0748 | 1.4233 | 21 | 10.1703
12 | 1.0942 | 1.8155 | 9 | 4.3587
13 | 1.1017 | 2.1864 | -81 | -39.2283
14 | 1.0972 | 1.881 | 3 | 1.4529
15 | 1.0942 | 1.7029 | 22 | 10.6546
16 | 1.0941 | 1.6977 | 5 | 2.4215
17 | 1.0093 | -3.8633 | 56 | 27.1208

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 28.9178 | -82.9183 | -28 | -13.5604 | 0.91784 | -96.4787 | 0.39029 | 0.13482 | 0.39029 | 0.98414 | -1.2539 | 1.0093 | -3.8633 | 66.3754
1 | 28.9178 | -82.9183 | -28 | -13.5604 | 0.91784 | -96.4787 | 0.39029 | 0.13482 | 0.39029 | 0.98414 | -1.2539 | 1.0093 | -3.8633 | 66.3754
2 | -41.2956 | -62.2228 | 41.7406 | 24.5351 | 0.44495 | -37.6877 | 0.30391 | 0.19354 | 0.30391 | 1.0748 | 1.4233 | 1.0942 | 1.8155 | 51.6853
3 | -50.7406 | -28.8938 | 50.9011 | 28.9276 | 0.16048 | 0.033868 | 0.2334 | 0.23243 | 0.2334 | 1.0942 | 1.8155 | 1.1017 | 2.1864 | 36.1861
4 | 15.4671 | 5.3569 | -15.4344 | -6.5065 | 0.032603 | -1.1495 | 0.064982 | 0.066773 | 0.066773 | 1.1017 | 2.1864 | 1.0972 | 1.881 | 10.3525
5 | 14.6319 | 4.9437 | -14.582 | -6.8884 | 0.049883 | -1.9447 | 0.061314 | 0.064464 | 0.064464 | 1.1017 | 2.1864 | 1.0942 | 1.7029 | 9.9944
6 | 12.4344 | 5.0536 | -12.4182 | -5.917 | 0.016242 | -0.86343 | 0.053508 | 0.054985 | 0.054985 | 1.0972 | 1.881 | 1.0942 | 1.7029 | 8.5248
7 | 2.174 | 0.91744 | -2.1739 | -1.0705 | 8.4607e-05 | -0.15308 | 0.009432 | 0.0096868 | 0.0096868 | 1.0942 | 1.7029 | 1.0941 | 1.6977 | 1.5018
8 | 2.8262 | 1.2334 | -2.8261 | -1.351 | 0.00010999 | -0.1176 | 0.012326 | 0.012522 | 0.012522 | 1.0942 | 1.7029 | 1.0941 | 1.6977 | 1.9414
9 | -9.9337 | -61.9996 | 9.9631 | 61.1965 | 0.029358 | -0.80311 | 0.16478 | 0.16234 | 0.16478 | 1 | 0 | 1.0023 | -0.0058512 | 17.1648
10 | -18.1143 | -36.4443 | 18.1437 | 34.2254 | 0.029374 | -2.2189 | 0.10656 | 0.10107 | 0.10656 | 1.0023 | -0.0058512 | 1.0059 | 0.049875 | 11.0997
11 | -18.8487 | -37.8283 | 18.8793 | 35.7071 | 0.030564 | -2.1212 | 0.11066 | 0.10538 | 0.11066 | 1.0023 | -0.0058512 | 1.0059 | 0.049875 | 11.5268
12 | 30.4486 | -10.7064 | -30.4374 | 9.3754 | 0.011141 | -1.331 | 0.08421 | 0.083078 | 0.08421 | 1.0059 | 0.049875 | 1.006 | -0.047711 | 8.7719
13 | 4.5 | 2.1793 | -4.4998 | -3.3172 | 0.00024775 | -1.1378 | 0.013041 | 0.014583 | 0.014583 | 1.0062 | -0.038016 | 1.006 | -0.047711 | 1.519
14 | -18 | -8.7174 | 18.0019 | 8.1112 | 0.0019027 | -0.60623 | 0.052185 | 0.051505 | 0.052185 | 1.0058 | -0.069396 | 1.006 | -0.047711 | 5.4359
15 | -43.9716 | -47.8451 | 44.1332 | 43.386 | 0.16166 | -4.4591 | 0.16954 | 0.15976 | 0.16954 | 1.0059 | 0.049875 | 1.0166 | 0.43464 | 17.6605
16 | -61.0647 | -51.9448 | 61.2798 | 48.5049 | 0.21512 | -3.4398 | 0.20913 | 0.20175 | 0.20913 | 1.006 | -0.047711 | 1.0166 | 0.43464 | 21.7839
17 | -29.4269 | -15.5383 | 29.4479 | 13.0258 | 0.020922 | -2.5125 | 0.085905 | 0.082964 | 0.085905 | 1.0166 | 0.43464 | 1.0186 | 0.57786 | 8.9484
18 | -30.5304 | -16.025 | 30.5521 | 13.6107 | 0.021707 | -2.4143 | 0.089011 | 0.086176 | 0.089011 | 1.0166 | 0.43464 | 1.0186 | 0.57786 | 9.2719
19 | -30.6256 | -34.2093 | 30.6615 | 32.0176 | 0.035898 | -2.1917 | 0.11853 | 0.11406 | 0.11853 | 1.0166 | 0.43464 | 1.02 | 0.55073 | 12.3467
20 | -29.8301 | -33.3828 | 29.8651 | 31.1235 | 0.034966 | -2.2593 | 0.11557 | 0.11098 | 0.11557 | 1.0166 | 0.43464 | 1.02 | 0.55073 | 12.0385
21 | -19.7212 | -51.8323 | 20.2956 | 52.0525 | 0.57442 | 0.22014 | 0.2338 | 0.22736 | 0.2338 | 1.0375 | 1.2778 | 1.0748 | 1.4233 | 36.2475

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 92.1289 | 57.4422 | -91.8357 | -50.6296 | 0.29321 | 6.8126 | 0.28492 | 0.46607 | 1 | 0 | 0.98414 | -1.2539 | 27.1424
1 | -60.5266 | -63.1411 | 60.7212 | 69.2671 | 0.19468 | 6.126 | 0.22503 | 0.38833 | 1.02 | 0.55073 | 1.0375 | 1.2778 | 22.1962

## res_ext_grid
| p_mw | q_mvar
0 | 82.1952 | -4.5574

## res_load
| p_mw | q_mvar
0 | 34 | 16.4662
1 | 0 | 200
2 | 27 | 13.0761
3 | 73.5 | 35.596
4 | 91 | 44.0713
5 | 56.5 | 27.363
6 | 34 | 16.4662
7 | 54 | 26.1522
8 | 36 | 19.8563
9 | 63 | 32.9324
10 | 21 | 10.1703
11 | 9 | 4.3587
12 | 11 | 5.3273
13 | 3 | 1.4529
14 | 22 | 10.6546
15 | 5 | 2.4215
16 | 101 | 48.9143

## res_sgen
| p_mw | q_mvar
0 | 97 | 46.9771
1 | 61 | 29.5423
2 | 16 | 7.7488
3 | 13 | 6.2959
4 | 104 | 50.3672
5 | 96 | 46.4928
6 | 39 | 18.8877
7 | 92 | 44.5556
8 | 45 | 21.7935

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | sgen | name | object
16 | sgen | bus | int64
17 | sgen | p_mw | float64
18 | sgen | q_mvar | float64
19 | sgen | sn_mva | float64
20 | sgen | scaling | float64
21 | sgen | in_service | bool
22 | sgen | type | object
23 | sgen | current_source | bool
24 | ext_grid | name | object
25 | ext_grid | bus | uint32
26 | ext_grid | vm_pu | float64
27 | ext_grid | va_degree | float64
28 | ext_grid | in_service | bool
29 | line | name | object
30 | line | std_type | object
31 | line | from_bus | uint32
32 | line | to_bus | uint32
33 | line | length_km | float64
34 | line | r_ohm_per_km | float64
35 | line | x_ohm_per_km | float64
36 | line | c_nf_per_km | float64
37 | line | g_us_per_km | float64
38 | line | max_i_ka | float64
39 | line | df | float64
40 | line | parallel | uint32
41 | line | type | object
42 | line | in_service | bool
43 | trafo | name | object
44 | trafo | std_type | object
45 | trafo | hv_bus | uint32
46 | trafo | lv_bus | uint32
47 | trafo | sn_mva | float64
48 | trafo | vn_hv_kv | float64
49 | trafo | vn_lv_kv | float64
50 | trafo | vk_percent | float64
51 | trafo | vkr_percent | float64
52 | trafo | pfe_kw | float64
53 | trafo | i0_percent | float64
54 | trafo | shift_degree | float64
55 | trafo | tap_side | object
56 | trafo | tap_neutral | float64
57 | trafo | tap_min | float64
58 | trafo | tap_max | float64
59 | trafo | tap_step_percent | float64
60 | trafo | tap_step_degree | float64
61 | trafo | tap_pos | float64
62 | trafo | tap_phase_shifter | bool
63 | trafo | parallel | uint32
64 | trafo | df | float64
65 | trafo | in_service | bool
66 | line_geodata | coords | object
67 | bus_geodata | x | float64
68 | bus_geodata | y | float64
69 | bus_geodata | coords | object
70 | res_bus | vm_pu | float64
71 | res_bus | va_degree | float64
72 | res_bus | p_mw | float64
73 | res_bus | q_mvar | float64
74 | res_line | p_from_mw | float64
75 | res_line | q_from_mvar | float64
76 | res_line | p_to_mw | float64
77 | res_line | q_to_mvar | float64
78 | res_line | pl_mw | float64
79 | res_line | ql_mvar | float64
80 | res_line | i_from_ka | float64
81 | res_line | i_to_ka | float64
82 | res_line | i_ka | float64
83 | res_line | vm_from_pu | float64
84 | res_line | va_from_degree | float64
85 | res_line | vm_to_pu | float64
86 | res_line | va_to_degree | float64
87 | res_line | loading_percent | float64
88 | res_trafo | p_hv_mw | float64
89 | res_trafo | q_hv_mvar | float64
90 | res_trafo | p_lv_mw | float64
91 | res_trafo | q_lv_mvar | float64
92 | res_trafo | pl_mw | float64
93 | res_trafo | ql_mvar | float64
94 | res_trafo | i_hv_ka | float64
95 | res_trafo | i_lv_ka | float64
96 | res_trafo | vm_hv_pu | float64
97 | res_trafo | va_hv_degree | float64
98 | res_trafo | vm_lv_pu | float64
99 | res_trafo | va_lv_degree | float64
100 | res_trafo | loading_percent | float64
101 | res_ext_grid | p_mw | float64
102 | res_ext_grid | q_mvar | float64
103 | res_load | p_mw | float64
104 | res_load | q_mvar | float64
105 | res_sgen | p_mw | float64
106 | res_sgen | q_mvar | float64